## DTx Zero Imp (hidden)
Terminals | 15 | Distance | XR=0 Load=0
Customers | 10
Vn | 253
Vt | 230.94 |  | 2Rc | 2Rc+j(Xt) | Im | In
Xt | 0 | 20 | 0.0013333 | 0.0013333 | 389.2941 | 375.8679
PLdref (kW) | 5 | 25 | 0.0016667 | 0.0016667 | 311.4353 | 300.6943
PLdAct | 6.05 | 30 | 0.002 | 0.002 | 259.5294 | 250.5786
Ild | 29.8913 | 35 | 0.0023333 | 0.0023333 | 222.4538 | 214.7817
ILdr | 23.913 | 40 | 0.0026667 | 0.0026667 | 194.6471 | 187.934
ILdni | 17.9348 | 45 | 0.003 | 0.003 | 173.0196 | 167.0524
Ld pf | 0.8 | 50 | 0.0033333 | 0.0033333 | 155.7176 | 150.3472
R Total | 0.5 | 55 | 0.0036667 | 0.0036667 | 141.5615 | 136.6792
X/R | 1 | 60 | 0.004 | 0.004 | 129.7647 | 125.2893
k | 65 | 65 | 0.0043333 | 0.0043333 | 119.7828 | 115.6517
V2 | 236.1306 | 70 | 0.0046667 | 0.0046667 | 111.2269 | 107.3908
|  | 75 | 0.005 | 0.005 | 103.8118 | 100.2314
Xt | 0.000244 | 80 | 0.0053333 | 0.0053333 | 97.3235 | 93.967
|  | 85 | 0.0056667 | 0.0056667 | 91.5986 | 88.4395
|  | 90 | 0.006 | 0.006 | 86.5098 | 83.5262
|  | 95 | 0.0063333 | 0.0063333 | 81.9567 | 79.1301
|  | 100 | 0.0066667 | 0.0066667 | 77.8588 | 75.1736
|  | 105 | 0.007 | 0.007 | 74.1513 | 71.5939
|  | 110 | 0.0073333 | 0.0073333 | 70.7807 | 68.3396
|  | 115 | 0.0076667 | 0.0076667 | 67.7033 | 65.3683
|  | 120 | 0.008 | 0.008 | 64.8824 | 62.6447
|  | 125 | 0.0083333 | 0.0083333 | 62.2871 | 60.1389
|  | 130 | 0.0086667 | 0.0086667 | 59.8914 | 57.8258
|  | 135 | 0.009 | 0.009 | 57.6732 | 55.6841
|  | 140 | 0.0093333 | 0.0093333 | 55.6134 | 53.6954
|  | 145 | 0.0096667 | 0.0096667 | 53.6957 | 51.8439
|  | 150 | 0.01 | 0.01 | 51.9059 | 50.1157
|  | 155 | 0.010333 | 0.010333 | 50.2315 | 48.4991
|  | 160 | 0.010667 | 0.010667 | 48.6618 | 46.9835
|  | 165 | 0.011 | 0.011 | 47.1872 | 45.5597
|  | 170 | 0.011333 | 0.011333 | 45.7993 | 44.2198
|  | 175 | 0.011667 | 0.011667 | 44.4908 | 42.9563
|  | 180 | 0.012 | 0.012 | 43.2549 | 41.7631
|  | 185 | 0.012333 | 0.012333 | 42.0859 | 40.6344
|  | 190 | 0.012667 | 0.012667 | 40.9783 | 39.565
|  | 195 | 0.013 | 0.013 | 39.9276 | 38.5506
|  | 200 | 0.013333 | 0.013333 | 38.9294 | 37.5868
|  | 205 | 0.013667 | 0.013667 | 37.9799 | 36.67
|  | 210 | 0.014 | 0.014 | 37.0756 | 35.7969
|  | 215 | 0.014333 | 0.014333 | 36.2134 | 34.9645
|  | 220 | 0.014667 | 0.014667 | 35.3904 | 34.1698
|  | 225 | 0.015 | 0.015 | 34.6039 | 33.4105
|  | 230 | 0.015333 | 0.015333 | 33.8517 | 32.6842
|  | 235 | 0.015667 | 0.015667 | 33.1314 | 31.9888
|  | 240 | 0.016 | 0.016 | 32.4412 | 31.3223
|  | 245 | 0.016333 | 0.016333 | 31.7791 | 30.6831
|  | 250 | 0.016667 | 0.016667 | 31.1435 | 30.0694
|  | 255 | 0.017 | 0.017 | 30.5329 | 29.4798
|  | 260 | 0.017333 | 0.017333 | 29.9457 | 28.9129
|  | 265 | 0.017667 | 0.017667 | 29.3807 | 28.3674
|  | 270 | 0.018 | 0.018 | 28.8366 | 27.8421
|  | 275 | 0.018333 | 0.018333 | 28.3123 | 27.3358
|  | 280 | 0.018667 | 0.018667 | 27.8067 | 26.8477
|  | 285 | 0.019 | 0.019 | 27.3189 | 26.3767
|  | 290 | 0.019333 | 0.019333 | 26.8479 | 25.9219
|  | 295 | 0.019667 | 0.019667 | 26.3928 | 25.4826
|  | 300 | 0.02 | 0.02 | 25.9529 | 25.0579
|  | 305 | 0.020333 | 0.020333 | 25.5275 | 24.6471
|  | 310 | 0.020667 | 0.020667 | 25.1157 | 24.2495
|  | 315 | 0.021 | 0.021 | 24.7171 | 23.8646
|  | 320 | 0.021333 | 0.021333 | 24.3309 | 23.4917
|  | 325 | 0.021667 | 0.021667 | 23.9566 | 23.1303
|  | 330 | 0.022 | 0.022 | 23.5936 | 22.7799
|  | 335 | 0.022333 | 0.022333 | 23.2414 | 22.4399
|  | 340 | 0.022667 | 0.022667 | 22.8997 | 22.1099
|  | 345 | 0.023 | 0.023 | 22.5678 | 21.7894
|  | 350 | 0.023333 | 0.023333 | 22.2454 | 21.4782
|  | 355 | 0.023667 | 0.023667 | 21.9321 | 21.1757
|  | 360 | 0.024 | 0.024 | 21.6275 | 20.8816
|  | 365 | 0.024333 | 0.024333 | 21.3312 | 20.5955
|  | 370 | 0.024667 | 0.024667 | 21.0429 | 20.3172
|  | 375 | 0.025 | 0.025 | 20.7624 | 20.0463
|  | 380 | 0.025333 | 0.025333 | 20.4892 | 19.7825
|  | 385 | 0.025667 | 0.025667 | 20.2231 | 19.5256
|  | 390 | 0.026 | 0.026 | 19.9638 | 19.2753
|  | 395 | 0.026333 | 0.026333 | 19.7111 | 19.0313
|  | 400 | 0.026667 | 0.026667 | 19.4647 | 18.7934
|  | 405 | 0.027 | 0.027 | 19.2244 | 18.5614
|  | 410 | 0.027333 | 0.027333 | 18.99 | 18.335
|  | 415 | 0.027667 | 0.027667 | 18.7612 | 18.1141
|  | 420 | 0.028 | 0.028 | 18.5378 | 17.8985
|  | 425 | 0.028333 | 0.028333 | 18.3197 | 17.6879
|  | 430 | 0.028667 | 0.028667 | 18.1067 | 17.4822
|  | 435 | 0.029 | 0.029 | 17.8986 | 17.2813
|  | 440 | 0.029333 | 0.029333 | 17.6952 | 17.0849
|  | 445 | 0.029667 | 0.029667 | 17.4964 | 16.8929
|  | 450 | 0.03 | 0.03 | 17.302 | 16.7052
|  | 455 | 0.030333 | 0.030333 | 17.1118 | 16.5217
|  | 460 | 0.030667 | 0.030667 | 16.9258 | 16.3421
|  | 465 | 0.031 | 0.031 | 16.7438 | 16.1664
|  | 470 | 0.031333 | 0.031333 | 16.5657 | 15.9944
|  | 475 | 0.031667 | 0.031667 | 16.3913 | 15.826
|  | 480 | 0.032 | 0.032 | 16.2206 | 15.6612
|  | 485 | 0.032333 | 0.032333 | 16.0534 | 15.4997
|  | 490 | 0.032667 | 0.032667 | 15.8896 | 15.3415
|  | 495 | 0.033 | 0.033 | 15.7291 | 15.1866
|  | 500 | 0.033333 | 0.033333 | 15.5718 | 15.0347

## Read me
Maximum PV generation estimation tool
Description:
This excel spreadsheet is a tool which estimates the maximum PV generation a low voltage feeder can accommodate without a breach of an upper voltage limit occurring for a given household load.
Feeder model:
The feeder model is such that there are two households connected to each terminal. The terminals are evenly distributed along the length of the feeder. The households are also evenly distributed across the three phases. For households to be evenly distributed across the three phases the number of terminals inputted into the tool needs to be a factor of three: 3, 6, 9, etc. There is an image of an example 3-terminal feeder embedded within the excel spreadsheet
Assumptions:
Each household includes both a load and a PV system, each PV system is of the same magnitude and each load is of the same magnitude. The PV systems inject power into the feeder at unity.
Inputs:
DTx no-load voltage and impedance, number of terminals (3, 6, 9…), household load (kW) and power factor, length of the feeder, feeder cable X/R ratio and resistance/km, upper voltage limit
Estimate:
The maximum PV generation estimate given is for each system, not the total installed PV on the feeder
Contact
For any enquiries regarding the spreadsheet or the related work, please contact Simon Heslop, s.heslop@student.unsw.edu.au

## Estimation
Terminals | 15 | Length | Rc | Xc | 0 DTx 0 Ld | FDR00 Sum |  |  |  | Angle shift cable |  |  |  | Angle shift DTx |  |  |  | AS | [5 empty] | Vtr | Vti | Vt | [5 empty] | IPVr | Estimation (A) | Estimation (kW)
C | 10 |  |  |  |  | Re | Im | [19 empty] | V21 | V22 | 2Rc | Im | In
Upper voltage limit | 253 | 20 | 0.00066667 | 0.00066667 | 375.8679 | -3758.6792 | 0 | -95094.5844 | 0 | 252.7494 | -0.25058 | -0.056804 | -4.8283 | 232.2272 | -51.4715 | 237.8629 | -12.9113 | 17.7396 | 114.5239 | 0 | 114.5239 | 1145.2392 | 28974.552 | 216.5442 | -51.0793 | 222.4871 | 225.1221 | 230.8442 | 0.0013333 | 626.7827 | 598.0816 | 114.5239 | 712.6055 | 180.2892
Xt | 0.0125 | 25 | 0.00083333 | 0.00083333 | 300.6943 | -3006.9434 | 0 | -76075.6675 | 0 | 252.7494 | -0.25058 | -0.056804 | -4.8283 | 231.9698 | -41.1772 | 235.5961 | -10.2788 | 15.1071 | 78.3684 | 0 | 78.3684 | 783.6838 | 19827.2011 | 221.238 | -40.9088 | 224.9884 | 228.7114 | 232.3412 | 0.0016667 | 441.1691 | 422.3905 | 78.3684 | 500.7589 | 126.692
Rt | 0.0003126 | 30 | 0.001 | 0.001 | 250.5786 | -2505.7861 | 0 | -63396.3896 | 0 | 252.7494 | -0.25058 | -0.056804 | -4.8283 | 231.7981 | -34.3143 | 234.3242 | -8.5443 | 13.3726 | 57.9546 | 0 | 57.9546 | 579.5458 | 14662.5098 | 223.8618 | -34.1158 | 226.4465 | 230.7179 | 233.2265 | 0.002 | 339.0039 | 325.2176 | 57.9546 | 383.1722 | 96.9426
DTx no load voltage | 230.94 | 35 | 0.0011667 | 0.0011667 | 214.7817 | -2147.8167 | 0 | -54339.7625 | 0 | 252.7494 | -0.25058 | -0.056804 | -4.8283 | 231.6755 | -29.4123 | 233.5351 | -7.3133 | 12.1416 | 45.1747 | 0 | 45.1747 | 451.7473 | 11429.2059 | 225.4893 | -29.2576 | 227.3795 | 231.9624 | 233.8003 | 0.0023333 | 275.1763 | 264.3232 | 45.1747 | 309.4979 | 78.303
Ω/km | 0.5 | 40 | 0.0013333 | 0.0013333 | 187.934 | -1879.3396 | 0 | -47547.2922 | 0 | 252.7494 | -0.25058 | -0.056804 | -4.8283 | 231.5836 | -25.7357 | 233.0092 | -6.3936 | 11.2219 | 36.5737 | 0 | 36.5737 | 365.7369 | 9253.1442 | 226.5752 | -25.6105 | 228.018 | 232.7928 | 234.1973 | 0.0026667 | 231.7239 | 222.7808 | 36.5737 | 259.3545 | 65.6167
Load pf | 1 | 45 | 0.0015 | 0.0015 | 167.0524 | -1670.5241 | 0 | -42264.2597 | 0 | 252.7494 | -0.25058 | -0.056804 | -4.8283 | 231.5121 | -22.8762 | 232.6396 | -5.68 | 10.5083 | 30.4668 | 0 | 30.4668 | 304.6677 | 7708.0935 | 227.34 | -22.7719 | 228.4776 | 233.3776 | 234.486 | 0.003 | 200.2789 | 192.6726 | 30.4668 | 223.1394 | 56.4543
Cable X/R ratio | 1 | 50 | 0.0016667 | 0.0016667 | 150.3472 | -1503.4717 | 0 | -38037.8337 | 0 | 252.7494 | -0.25058 | -0.056804 | -4.8283 | 231.4549 | -20.5886 | 232.3688 | -5.1101 | 9.9384 | 25.9484 | 0 | 25.9484 | 259.4838 | 6564.9406 | 227.9015 | -20.4997 | 228.8216 | 233.807 | 234.704 | 0.0033333 | 176.4714 | 169.8511 | 25.9484 | 195.7995 | 49.5373
Power Load | 0 | 55 | 0.0018333 | 0.0018333 | 136.6792 | -1366.7924 | 0 | -34579.8489 | 0 | 252.7494 | -0.25058 | -0.056804 | -4.8283 | 231.4081 | -18.7169 | 232.1638 | -4.6444 | 9.4727 | 22.4943 | 0 | 22.4943 | 224.9431 | 5691.0593 | 228.3277 | -18.6399 | 229.0873 | 234.1329 | 234.8737 | 0.0036667 | 157.813 | 151.9497 | 22.4943 | 174.444 | 44.1343
PLd | 0 | 60 | 0.002 | 0.002 | 125.2893 | -1252.8931 | 0 | -31698.1948 | 0 | 252.7494 | -0.25058 | -0.056804 | -4.8283 | 231.3691 | -17.1572 | 232.0043 | -4.2566 | 9.0849 | 19.7829 | 0 | 19.7829 | 197.8288 | 5005.0679 | 228.66 | -17.0894 | 229.2977 | 234.3871 | 235.0092 | 0.004 | 142.788 | 137.5241 | 19.7829 | 157.3069 | 39.7987
Ild | 0 | 65 | 0.0021667 | 0.0021667 | 115.6517 | -1156.5167 | 0 | -29259.8721 | 0 | 252.7494 | -0.25058 | -0.056804 | -4.8283 | 231.3361 | -15.8374 | 231.8775 | -3.9286 | 8.757 | 17.6072 | 0 | 17.6072 | 176.0719 | 4454.619 | 228.9249 | -15.7771 | 229.4679 | 234.5896 | 235.1196 | 0.0043333 | 130.4225 | 125.645 | 17.6072 | 143.2521 | 36.2428
ILdr | 0 | 70 | 0.0023333 | 0.0023333 | 107.3908 | -1073.9083 | 0 | -27169.8812 | 0 | 252.7494 | -0.25058 | -0.056804 | -4.8283 | 231.3078 | -14.7061 | 231.7748 | -3.6477 | 8.476 | 15.8289 | 0 | 15.8289 | 158.2887 | 4004.7052 | 229.1402 | -14.6519 | 229.6081 | 234.7542 | 235.211 | 0.0046667 | 120.0624 | 115.6877 | 15.8289 | 131.5165 | 33.2737
ILdni | 0 | 75 | 0.0025 | 0.0025 | 100.2314 | -1002.3145 | 0 | -25358.5558 | 0 | 252.7494 | -0.25058 | -0.056804 | -4.8283 | 231.2833 | -13.7257 | 231.6902 | -3.4043 | 8.2326 | 14.3523 | 0 | 14.3523 | 143.5232 | 3631.1376 | 229.3178 | -13.6766 | 229.7253 | 234.8901 | 235.2879 | 0.005 | 111.2525 | 107.2169 | 14.3523 | 121.5692 | 30.757
k | 65 | 80 | 0.0026667 | 0.0026667 | 93.967 | -939.6698 | 0 | -23773.6461 | 0 | 252.7494 | -0.25058 | -0.056804 | -4.8283 | 231.2618 | -12.8679 | 231.6195 | -3.1913 | 8.0197 | 13.1096 | 0 | 13.1096 | 131.0961 | 3316.7301 | 229.4666 | -12.823 | 229.8246 | 235.0038 | 235.3534 | 0.0053333 | 103.6661 | 99.9201 | 13.1096 | 113.0297 | 28.5965
|  | 85 | 0.0028333 | 0.0028333 | 88.4395 | -884.3951 | 0 | -22375.1963 | 0 | 252.7494 | -0.25058 | -0.056804 | -4.8283 | 231.2429 | -12.1109 | 231.5598 | -3.0035 | 7.8318 | 12.0513 | 0 | 12.0513 | 120.5129 | 3048.9758 | 229.5926 | -12.0697 | 229.9096 | 235.1002 | 235.4098 | 0.0056667 | 97.0626 | 93.5669 | 12.0513 | 105.6182 | 26.7214
|  | 90 | 0.003 | 0.003 | 83.5262 | -835.262 | 0 | -21132.1299 | 0 | 252.7494 | -0.25058 | -0.056804 | -4.8283 | 231.226 | -11.4381 | 231.5088 | -2.8366 | 7.6649 | 11.1406 | 0 | 11.1406 | 111.4063 | 2818.5804 | 229.7004 | -11.4 | 229.9832 | 235.1827 | 235.4588 | 0.006 | 91.2611 | 87.9838 | 11.1406 | 99.1244 | 25.0785
|  | 95 | 0.0031667 | 0.0031667 | 79.1301 | -791.3009 | 0 | -20019.9125 | 0 | 252.7494 | -0.25058 | -0.056804 | -4.8283 | 231.211 | -10.8361 | 231.4648 | -2.6872 | 7.5155 | 10.3498 | 0 | 10.3498 | 103.4984 | 2618.5088 | 229.7937 | -10.8007 | 230.0474 | 235.254 | 235.5018 | 0.0063333 | 86.1226 | 83.0376 | 10.3498 | 93.3875 | 23.627
|  | 100 | 0.0033333 | 0.0033333 | 75.1736 | -751.7358 | 0 | -19018.9169 | 0 | 252.7494 | -0.25058 | -0.056804 | -4.8283 | 231.1974 | -10.2943 | 231.4265 | -2.5528 | 7.3812 | 9.6575 | 0 | 9.6575 | 96.575 | 2443.3486 | 229.8749 | -10.2612 | 230.1038 | 235.3161 | 235.5397 | 0.0066667 | 81.5386 | 78.6244 | 9.6575 | 88.2819 | 22.3353
|  | 105 | 0.0035 | 0.0035 | 71.5939 | -715.9389 | 0 | -18113.2542 | 0 | 252.7494 | -0.25058 | -0.056804 | -4.8283 | 231.1852 | -9.8041 | 231.393 | -2.4313 | 7.2596 | 9.0469 | 0 | 9.0469 | 90.4694 | 2288.8749 | 229.9463 | -9.7731 | 230.1539 | 235.3707 | 235.5735 | 0.007 | 77.4232 | 74.6616 | 9.0469 | 83.7086 | 21.1783
|  | 110 | 0.0036667 | 0.0036667 | 68.3396 | -683.3962 | 0 | -17289.9244 | 0 | 252.7494 | -0.25058 | -0.056804 | -4.8283 | 231.174 | -9.3585 | 231.3634 | -2.3207 | 7.149 | 8.5049 | 0 | 8.5049 | 85.0493 | 2151.7462 | 230.0094 | -9.3293 | 230.1985 | 235.4189 | 235.6037 | 0.0073333 | 73.7075 | 71.0832 | 8.5049 | 79.5882 | 20.1358
|  | 115 | 0.0038333 | 0.0038333 | 65.3683 | -653.6833 | 0 | -16538.1886 | 0 | 252.7494 | -0.25058 | -0.056804 | -4.8283 | 231.1639 | -8.9516 | 231.3371 | -2.2198 | 7.0481 | 8.0209 | 0 | 8.0209 | 80.2091 | 2029.289 | 230.0655 | -8.9241 | 230.2385 | 235.4618 | 235.6309 | 0.0076667 | 70.3356 | 67.8354 | 8.0209 | 75.8563 | 19.1917
|  | 120 | 0.004 | 0.004 | 62.6447 | -626.4465 | 0 | -15849.0974 | 0 | 252.7494 | -0.25058 | -0.056804 | -4.8283 | 231.1545 | -8.5786 | 231.3137 | -2.1273 | 6.9556 | 7.5863 | 0 | 7.5863 | 75.8633 | 1919.3406 | 230.1157 | -8.5526 | 230.2745 | 235.5002 | 235.6555 | 0.008 | 67.2615 | 64.8741 | 7.5863 | 72.4604 | 18.3325
|  | 125 | 0.0041667 | 0.0041667 | 60.1389 | -601.3887 | 0 | -15215.1335 | 0 | 252.7494 | -0.25058 | -0.056804 | -4.8283 | 231.146 | -8.2354 | 231.2926 | -2.0422 | 6.8706 | 7.1942 | 0 | 7.1942 | 71.9421 | 1820.135 | 230.1608 | -8.2108 | 230.3072 | 235.5347 | 235.6778 | 0.0083333 | 64.4472 | 62.1627 | 7.1942 | 69.3569 | 17.5473
|  | 130 | 0.0043333 | 0.0043333 | 57.8258 | -578.2583 | 0 | -14629.9361 | 0 | 252.7494 | -0.25058 | -0.056804 | -4.8283 | 231.138 | -7.9187 | 231.2736 | -1.9637 | 6.792 | 6.8388 | 0 | 6.8388 | 68.388 | 1730.217 | 230.2015 | -7.8953 | 230.3369 | 235.5659 | 235.6981 | 0.0086667 | 61.8608 | 59.6707 | 6.8388 | 66.5095 | 16.8269
|  | 135 | 0.0045 | 0.0045 | 55.6841 | -556.8414 | 0 | -14088.0866 | 0 | 252.7494 | -0.25058 | -0.056804 | -4.8283 | 231.1307 | -7.6254 | 231.2564 | -1.891 | 6.7193 | 6.5153 | 0 | 6.5153 | 65.1533 | 1648.3776 | 230.2385 | -7.6031 | 230.364 | 235.5941 | 235.7168 | 0.009 | 59.4755 | 57.3722 | 6.5153 | 63.8876 | 16.1636
|  | 140 | 0.0046667 | 0.0046667 | 53.6954 | -536.9542 | 0 | -13584.9406 | 0 | 252.7494 | -0.25058 | -0.056804 | -4.8283 | 231.1239 | -7.3531 | 231.2408 | -1.8234 | 6.6518 | 6.2198 | 0 | 6.2198 | 62.1978 | 1573.6049 | 230.2721 | -7.3318 | 230.3888 | 235.6199 | 235.7339 | 0.0093333 | 57.2688 | 55.2455 | 6.2198 | 61.4653 | 15.5507
|  | 145 | 0.0048333 | 0.0048333 | 51.8439 | -518.4385 | 0 | -13116.4944 | 0 | 252.7494 | -0.25058 | -0.056804 | -4.8283 | 231.1175 | -7.0995 | 231.2266 | -1.7606 | 6.5889 | 5.9488 | 0 | 5.9488 | 59.488 | 1505.0462 | 230.3029 | -7.0791 | 230.4117 | 235.6434 | 235.7497 | 0.0096667 | 55.221 | 53.272 | 5.9488 | 59.2208 | 14.9829
|  | 150 | 0.005 | 0.005 | 50.1157 | -501.1572 | 0 | -12679.2779 | 0 | 252.7494 | -0.25058 | -0.056804 | -4.8283 | 231.1116 | -6.8629 | 231.2135 | -1.7019 | 6.5302 | 5.6995 | 0 | 5.6995 | 56.9952 | 1441.978 | 230.3311 | -6.8433 | 230.4328 | 235.665 | 235.7643 | 0.01 | 53.3155 | 51.4354 | 5.6995 | 57.1349 | 14.4551
|  | 155 | 0.0051667 | 0.0051667 | 48.4991 | -484.9909 | 0 | -12270.269 | 0 | 252.7494 | -0.25058 | -0.056804 | -4.8283 | 231.1061 | -6.6415 | 231.2015 | -1.647 | 6.4753 | 5.4695 | 0 | 5.4695 | 54.695 | 1383.7829 | 230.3571 | -6.6228 | 230.4523 | 235.6848 | 235.7779 | 0.010333 | 51.538 | 49.722 | 5.4695 | 55.1915 | 13.9635
|  | 160 | 0.0053333 | 0.0053333 | 46.9835 | -469.8349 | 0 | -11886.823 | 0 | 252.7494 | -0.25058 | -0.056804 | -4.8283 | 231.1009 | -6.4339 | 231.1904 | -1.5955 | 6.4239 | 5.2566 | 0 | 5.2566 | 52.5664 | 1329.9311 | 230.3811 | -6.4159 | 230.4704 | 235.7032 | 235.7905 | 0.010667 | 49.8758 | 48.1198 | 5.2566 | 53.3764 | 13.5042
|  | 165 | 0.0055 | 0.0055 | 45.5597 | -455.5975 | 0 | -11526.6163 | 0 | 252.7494 | -0.25058 | -0.056804 | -4.8283 | 231.096 | -6.239 | 231.1802 | -1.5472 | 6.3755 | 5.0592 | 0 | 5.0592 | 50.5915 | 1279.9656 | 230.4032 | -6.2216 | 230.4872 | 235.7201 | 235.8022 | 0.011 | 48.3181 | 46.6181 | 5.0592 | 51.6773 | 13.0744
|  | 170 | 0.0056667 | 0.0056667 | 44.2198 | -442.1976 | 0 | -11187.5982 | 0 | 252.7494 | -0.25058 | -0.056804 | -4.8283 | 231.0914 | -6.0555 | 231.1708 | -1.5017 | 6.33 | 4.8755 | 0 | 4.8755 | 48.7546 | 1233.4903 | 230.4238 | -6.0388 | 230.5029 | 235.7358 | 235.8132 | 0.011333 | 46.8553 | 45.2079 | 4.8755 | 50.0833 | 12.6711
|  | 175 | 0.0058333 | 0.0058333 | 42.9563 | -429.5633 | 0 | -10867.9525 | 0 | 252.7494 | -0.25058 | -0.056804 | -4.8283 | 231.0871 | -5.8825 | 231.162 | -1.4588 | 6.2871 | 4.7042 | 0 | 4.7042 | 47.0419 | 1190.1601 | 230.4429 | -5.8663 | 230.5176 | 235.7505 | 235.8234 | 0.011667 | 45.4789 | 43.8808 | 4.7042 | 48.585 | 12.292
|  | 180 | 0.006 | 0.006 | 41.7631 | -417.631 | 0 | -10566.0649 | 0 | 252.7494 | -0.25058 | -0.056804 | -4.8283 | 231.083 | -5.7191 | 231.1538 | -1.4183 | 6.2466 | 4.5442 | 0 | 4.5442 | 45.4416 | 1149.6734 | 230.4607 | -5.7035 | 230.5313 | 235.7641 | 235.8331 | 0.012 | 44.1814 | 42.6298 | 4.5442 | 47.174 | 11.935
|  | 185 | 0.0061667 | 0.0061667 | 40.6344 | -406.3437 | 0 | -10280.4956 | 0 | 252.7494 | -0.25058 | -0.056804 | -4.8283 | 231.0792 | -5.5645 | 231.1461 | -1.38 | 6.2083 | 4.3943 | 0 | 4.3943 | 43.9433 | 1111.7652 | 230.4774 | -5.5494 | 230.5442 | 235.7768 | 235.8421 | 0.012333 | 42.9562 | 41.4485 | 4.3943 | 45.8428 | 11.5982
|  | 190 | 0.0063333 | 0.0063333 | 39.565 | -395.6504 | 0 | -10009.9562 | 0 | 252.7494 | -0.25058 | -0.056804 | -4.8283 | 231.0755 | -5.4181 | 231.139 | -1.3437 | 6.172 | 4.2538 | 0 | 4.2538 | 42.5376 | 1076.2021 | 230.493 | -5.4035 | 230.5563 | 235.7888 | 235.8507 | 0.012667 | 41.7975 | 40.3312 | 4.2538 | 44.5849 | 11.28
|  | 195 | 0.0065 | 0.0065 | 38.5506 | -385.5056 | 0 | -9753.2907 | 0 | 252.7494 | -0.25058 | -0.056804 | -4.8283 | 231.072 | -5.2791 | 231.1323 | -1.3092 | 6.1375 | 4.1217 | 0 | 4.1217 | 41.2165 | 1042.7775 | 230.5076 | -5.265 | 230.5677 | 235.7999 | 235.8587 | 0.013 | 40.6999 | 39.2728 | 4.1217 | 43.3944 | 10.9788
|  | 200 | 0.0066667 | 0.0066667 | 37.5868 | -375.8679 | 0 | -9509.4584 | 0 | 252.7494 | -0.25058 | -0.056804 | -4.8283 | 231.0687 | -5.1471 | 231.126 | -1.2765 | 6.1048 | 3.9973 | 0 | 3.9973 | 39.9726 | 1011.3079 | 230.5213 | -5.1335 | 230.5785 | 235.8104 | 235.8663 | 0.013333 | 39.6586 | 38.2687 | 3.9973 | 42.2659 | 10.6933
|  | 205 | 0.0068333 | 0.0068333 | 36.67 | -366.7004 | 0 | -9277.5204 | 0 | 252.7494 | -0.25058 | -0.056804 | -4.8283 | 231.0656 | -5.0216 | 231.1201 | -1.2454 | 6.0737 | 3.88 | 0 | 3.88 | 38.7996 | 981.6301 | 230.5343 | -5.0083 | 230.5887 | 235.8203 | 235.8735 | 0.013667 | 38.6695 | 37.3149 | 3.88 | 41.1948 | 10.4223
|  | 210 | 0.007 | 0.007 | 35.7969 | -357.9694 | 0 | -9056.6271 | 0 | 252.7494 | -0.25058 | -0.056804 | -4.8283 | 231.0626 | -4.902 | 231.1146 | -1.2157 | 6.044 | 3.7692 | 0 | 3.7692 | 37.6916 | 953.5982 | 230.5464 | -4.8891 | 230.5983 | 235.8296 | 235.8803 | 0.014 | 37.7288 | 36.4076 | 3.7692 | 40.1768 | 10.1647
|  | 215 | 0.0071667 | 0.0071667 | 34.9645 | -349.6446 | 0 | -8846.0078 | 0 | 252.7494 | -0.25058 | -0.056804 | -4.8283 | 231.0597 | -4.788 | 231.1093 | -1.1875 | 6.0158 | 3.6644 | 0 | 3.6644 | 36.6435 | 927.0815 | 230.5579 | -4.7755 | 230.6074 | 235.8384 | 235.8868 | 0.014333 | 36.8329 | 35.5436 | 3.6644 | 39.2079 | 9.9196
|  | 220 | 0.0073333 | 0.0073333 | 34.1698 | -341.6981 | 0 | -8644.9622 | 0 | 252.7494 | -0.25058 | -0.056804 | -4.8283 | 231.057 | -4.6792 | 231.1044 | -1.1605 | 5.9888 | 3.5651 | 0 | 3.5651 | 35.6507 | 901.9628 | 230.5688 | -4.667 | 230.616 | 235.8467 | 235.8929 | 0.014667 | 35.9787 | 34.7197 | 3.5651 | 38.2848 | 9.686
|  | 225 | 0.0075 | 0.0075 | 33.4105 | -334.1048 | 0 | -8452.8519 | 0 | 252.7494 | -0.25058 | -0.056804 | -4.8283 | 231.0544 | -4.5752 | 231.0997 | -1.1347 | 5.963 | 3.4709 | 0 | 3.4709 | 34.7089 | 878.1361 | 230.5791 | -4.5634 | 230.6243 | 235.8546 | 235.8988 | 0.015 | 35.1633 | 33.9333 | 3.4709 | 37.4042 | 9.4633
|  | 230 | 0.0076667 | 0.0076667 | 32.6842 | -326.8417 | 0 | -8269.0943 | 0 | 252.7494 | -0.25058 | -0.056804 | -4.8283 | 231.0519 | -4.4758 | 231.0953 | -1.11 | 5.9383 | 3.3814 | 0 | 3.3814 | 33.8145 | 855.5062 | 230.5889 | -4.4642 | 230.6321 | 235.8621 | 235.9043 | 0.015333 | 34.3842 | 33.1819 | 3.3814 | 36.5633 | 9.2505
|  | 235 | 0.0078333 | 0.0078333 | 31.9888 | -319.8876 | 0 | -8093.1561 | 0 | 252.7494 | -0.25058 | -0.056804 | -4.8283 | 231.0495 | -4.3806 | 231.0911 | -1.0864 | 5.9147 | 3.2964 | 0 | 3.2964 | 32.9639 | 833.9865 | 230.5981 | -4.3693 | 230.6395 | 235.8692 | 235.9096 | 0.015667 | 33.6389 | 32.4631 | 3.2964 | 35.7594 | 9.0471
|  | 240 | 0.008 | 0.008 | 31.3223 | -313.2233 | 0 | -7924.5487 | 0 | 252.7494 | -0.25058 | -0.056804 | -4.8283 | 231.0473 | -4.2893 | 231.0871 | -1.0638 | 5.8921 | 3.2154 | 0 | 3.2154 | 32.1541 | 813.4986 | 230.6069 | -4.2783 | 230.6466 | 235.8759 | 235.9147 | 0.016 | 32.9254 | 31.7748 | 3.2154 | 34.9902 | 8.8525
|  | 245 | 0.0081667 | 0.0081667 | 30.6831 | -306.831 | 0 | -7762.8232 | 0 | 252.7494 | -0.25058 | -0.056804 | -4.8283 | 231.0451 | -4.2018 | 231.0833 | -1.0421 | 5.8704 | 3.1382 | 0 | 3.1382 | 31.3823 | 793.9713 | 230.6153 | -4.191 | 230.6534 | 235.8823 | 235.9195 | 0.016333 | 32.2416 | 31.1153 | 3.1382 | 34.2535 | 8.6661
|  | 250 | 0.0083333 | 0.0083333 | 30.0694 | -300.6943 | 0 | -7607.5667 | 0 | 252.7494 | -0.25058 | -0.056804 | -4.8283 | 231.043 | -4.1177 | 231.0797 | -1.0213 | 5.8496 | 3.0646 | 0 | 3.0646 | 30.6458 | 775.3397 | 230.6233 | -4.1072 | 230.6599 | 235.8884 | 235.9242 | 0.016667 | 31.5857 | 30.4826 | 3.0646 | 33.5472 | 8.4874
|  | 255 | 0.0085 | 0.0085 | 29.4798 | -294.7984 | 0 | -7458.3988 | 0 | 252.7494 | -0.25058 | -0.056804 | -4.8283 | 231.041 | -4.037 | 231.0762 | -1.0012 | 5.8295 | 2.9942 | 0 | 2.9942 | 29.9425 | 757.5444 | 230.6309 | -4.0267 | 230.6661 | 235.8942 | 235.9286 | 0.017 | 30.956 | 29.8752 | 2.9942 | 32.8694 | 8.316
|  | 260 | 0.0086667 | 0.0086667 | 28.9129 | -289.1292 | 0 | -7314.968 | 0 | 252.7494 | -0.25058 | -0.056804 | -4.8283 | 231.039 | -3.9593 | 231.0729 | -0.98198 | 5.8103 | 2.927 | 0 | 2.927 | 29.27 | 740.5313 | 230.6382 | -3.9493 | 230.672 | 235.8998 | 235.9328 | 0.017333 | 30.351 | 29.2916 | 2.927 | 32.2186 | 8.1513
|  | 265 | 0.0088333 | 0.0088333 | 28.3674 | -283.6739 | 0 | -7176.9498 | 0 | 252.7494 | -0.25058 | -0.056804 | -4.8283 | 231.0371 | -3.8846 | 231.0698 | -0.96346 | 5.7918 | 2.8627 | 0 | 2.8627 | 28.6265 | 724.2505 | 230.6451 | -3.8748 | 230.6777 | 235.9051 | 235.9369 | 0.017667 | 29.7693 | 28.7304 | 2.8627 | 31.5931 | 7.993
|  | 270 | 0.009 | 0.009 | 27.8421 | -278.4207 | 0 | -7044.0433 | 0 | 252.7494 | -0.25058 | -0.056804 | -4.8283 | 231.0353 | -3.8127 | 231.0668 | -0.94562 | 5.7739 | 2.801 | 0 | 2.801 | 28.0101 | 708.6567 | 230.6518 | -3.8031 | 230.6831 | 235.9102 | 235.9408 | 0.018 | 29.2095 | 28.1904 | 2.801 | 30.9914 | 7.8408
|  | 275 | 0.0091667 | 0.0091667 | 27.3358 | -273.3585 | 0 | -6915.9698 | 0 | 252.7494 | -0.25058 | -0.056804 | -4.8283 | 231.0336 | -3.7434 | 231.0639 | -0.92843 | 5.7567 | 2.7419 | 0 | 2.7419 | 27.4193 | 693.7076 | 230.6581 | -3.734 | 230.6884 | 235.915 | 235.9446 | 0.018333 | 28.6704 | 27.6703 | 2.7419 | 30.4122 | 7.6943
|  | 280 | 0.0093333 | 0.0093333 | 26.8477 | -268.4771 | 0 | -6792.4703 | 0 | 252.7494 | -0.25058 | -0.056804 | -4.8283 | 231.0319 | -3.6765 | 231.0612 | -0.91186 | 5.7402 | 2.6852 | 0 | 2.6852 | 26.8524 | 679.3649 | 230.6642 | -3.6673 | 230.6934 | 235.9197 | 235.9482 | 0.018667 | 28.1509 | 27.1691 | 2.6852 | 29.8544 | 7.5532
|  | 285 | 0.0095 | 0.0095 | 26.3767 | -263.767 | 0 | -6673.3042 | 0 | 252.7494 | -0.25058 | -0.056804 | -4.8283 | 231.0303 | -3.612 | 231.0586 | -0.89586 | 5.7242 | 2.6308 | 0 | 2.6308 | 26.308 | 665.5927 | 230.6701 | -3.603 | 230.6982 | 235.9242 | 235.9517 | 0.019 | 27.6499 | 26.6858 | 2.6308 | 29.3166 | 7.4171
|  | 290 | 0.0096667 | 0.0096667 | 25.9219 | -259.2193 | 0 | -6558.2472 | 0 | 252.7494 | -0.25058 | -0.056804 | -4.8283 | 231.0288 | -3.5498 | 231.056 | -0.88042 | 5.7087 | 2.5785 | 0 | 2.5785 | 25.7849 | 652.3582 | 230.6757 | -3.5409 | 230.7028 | 235.9285 | 235.955 | 0.019333 | 27.1664 | 26.2194 | 2.5785 | 28.7979 | 7.2859
|  | 295 | 0.0098333 | 0.0098333 | 25.4826 | -254.8257 | 0 | -6447.0905 | 0 | 252.7494 | -0.25058 | -0.056804 | -4.8283 | 231.0273 | -3.4896 | 231.0536 | -0.8655 | 5.6938 | 2.5282 | 0 | 2.5282 | 25.2819 | 639.6308 | 230.6811 | -3.4809 | 230.7073 | 235.9326 | 235.9583 | 0.019667 | 26.6997 | 25.7691 | 2.5282 | 28.2973 | 7.1592
|  | 300 | 0.01 | 0.01 | 25.0579 | -250.5786 | 0 | -6339.639 | 0 | 252.7494 | -0.25058 | -0.056804 | -4.8283 | 231.0258 | -3.4314 | 231.0513 | -0.85108 | 5.6794 | 2.4798 | 0 | 2.4798 | 24.7977 | 627.3824 | 230.6862 | -3.4229 | 230.7116 | 235.9365 | 235.9614 | 0.02 | 26.2487 | 25.334 | 2.4798 | 27.8138 | 7.0369
|  | 305 | 0.010167 | 0.010167 | 24.6471 | -246.4708 | 0 | -6235.7105 | 0 | 252.7494 | -0.25058 | -0.056804 | -4.8283 | 231.0244 | -3.3752 | 231.0491 | -0.83713 | 5.6654 | 2.4331 | 0 | 2.4331 | 24.3315 | 615.5868 | 230.6912 | -3.3668 | 230.7158 | 235.9403 | 235.9644 | 0.020333 | 25.8127 | 24.9134 | 2.4331 | 27.3465 | 6.9187
|  | 310 | 0.010333 | 0.010333 | 24.2495 | -242.4954 | 0 | -6135.1345 | 0 | 252.7494 | -0.25058 | -0.056804 | -4.8283 | 231.023 | -3.3207 | 231.0469 | -0.82363 | 5.6519 | 2.3882 | 0 | 2.3882 | 23.8822 | 604.2195 | 230.696 | -3.3126 | 230.7198 | 235.944 | 235.9673 | 0.020667 | 25.391 | 24.5065 | 2.3882 | 26.8947 | 6.8044
|  | 315 | 0.0105 | 0.0105 | 23.8646 | -238.6463 | 0 | -6037.7514 | 0 | 252.7494 | -0.25058 | -0.056804 | -4.8283 | 231.0217 | -3.268 | 231.0448 | -0.81056 | 5.6389 | 2.3449 | 0 | 2.3449 | 23.4489 | 593.2581 | 230.7006 | -3.26 | 230.7236 | 235.9475 | 235.97 | 0.021 | 24.9829 | 24.1128 | 2.3449 | 26.4577 | 6.6938
|  | 320 | 0.010667 | 0.010667 | 23.4917 | -234.9175 | 0 | -5943.4115 | 0 | 252.7494 | -0.25058 | -0.056804 | -4.8283 | 231.0204 | -3.217 | 231.0428 | -0.7979 | 5.6262 | 2.3031 | 0 | 2.3031 | 23.0309 | 582.6813 | 230.7051 | -3.2091 | 230.7274 | 235.9509 | 235.9728 | 0.021333 | 24.5877 | 23.7315 | 2.3031 | 26.0346 | 6.5867
|  | 325 | 0.010833 | 0.010833 | 23.1303 | -231.3033 | 0 | -5851.9744 | 0 | 252.7494 | -0.25058 | -0.056804 | -4.8283 | 231.0192 | -3.1675 | 231.0409 | -0.78562 | 5.6139 | 2.2627 | 0 | 2.2627 | 22.6273 | 572.4695 | 230.7094 | -3.1597 | 230.731 | 235.9542 | 235.9754 | 0.021667 | 24.2048 | 23.3621 | 2.2627 | 25.6248 | 6.4831
|  | 330 | 0.011 | 0.011 | 22.7799 | -227.7987 | 0 | -5763.3081 | 0 | 252.7494 | -0.25058 | -0.056804 | -4.8283 | 231.018 | -3.1195 | 231.0391 | -0.77372 | 5.602 | 2.2237 | 0 | 2.2237 | 22.2373 | 562.6043 | 230.7135 | -3.1119 | 230.7345 | 235.9574 | 235.9779 | 0.022 | 23.8337 | 23.004 | 2.2237 | 25.2278 | 6.3826
|  | 335 | 0.011167 | 0.011167 | 22.4399 | -224.3988 | 0 | -5677.2886 | 0 | 252.7494 | -0.25058 | -0.056804 | -4.8283 | 231.0168 | -3.0729 | 231.0373 | -0.76218 | 5.5905 | 2.186 | 0 | 2.186 | 21.8604 | 553.0687 | 230.7175 | -3.0654 | 230.7379 | 235.9604 | 235.9803 | 0.022333 | 23.4738 | 22.6568 | 2.186 | 24.8428 | 6.2852
|  | 340 | 0.011333 | 0.011333 | 22.1099 | -221.0988 | 0 | -5593.7991 | 0 | 252.7494 | -0.25058 | -0.056804 | -4.8283 | 231.0157 | -3.0277 | 231.0356 | -0.75097 | 5.5793 | 2.1496 | 0 | 2.1496 | 21.4959 | 543.8465 | 230.7214 | -3.0204 | 230.7411 | 235.9634 | 235.9827 | 0.022667 | 23.1247 | 22.3199 | 2.1496 | 24.4695 | 6.1908
|  | 345 | 0.0115 | 0.0115 | 21.7894 | -217.8944 | 0 | -5512.7295 | 0 | 252.7494 | -0.25058 | -0.056804 | -4.8283 | 231.0146 | -2.9839 | 231.0339 | -0.74009 | 5.5684 | 2.1143 | 0 | 2.1143 | 21.1432 | 534.9226 | 230.7251 | -2.9766 | 230.7443 | 235.9662 | 235.985 | 0.023 | 22.7858 | 21.9929 | 2.1143 | 24.1072 | 6.0991
|  | 350 | 0.011667 | 0.011667 | 21.4782 | -214.7817 | 0 | -5433.9762 | 0 | 252.7494 | -0.25058 | -0.056804 | -4.8283 | 231.0136 | -2.9412 | 231.0323 | -0.72952 | 5.5578 | 2.0802 | 0 | 2.0802 | 20.8017 | 526.2831 | 230.7287 | -2.9341 | 230.7473 | 235.969 | 235.9872 | 0.023333 | 22.4567 | 21.6754 | 2.0802 | 23.7555 | 6.0102
|  | 355 | 0.011833 | 0.011833 | 21.1757 | -211.7566 | 0 | -5357.4414 | 0 | 252.7494 | -0.25058 | -0.056804 | -4.8283 | 231.0125 | -2.8998 | 231.0307 | -0.71925 | 5.5476 | 2.0471 | 0 | 2.0471 | 20.4709 | 517.9146 | 230.7322 | -2.8928 | 230.7503 | 235.9717 | 235.9894 | 0.023667 | 22.137 | 21.3669 | 2.0471 | 23.414 | 5.9237
|  | 360 | 0.012 | 0.012 | 20.8816 | -208.8155 | 0 | -5283.0325 | 0 | 252.7494 | -0.25058 | -0.056804 | -4.8283 | 231.0115 | -2.8595 | 231.0292 | -0.70926 | 5.5376 | 2.015 | 0 | 2.015 | 20.1504 | 509.8047 | 230.7356 | -2.8526 | 230.7532 | 235.9743 | 235.9915 | 0.024 | 21.8262 | 21.0671 | 2.015 | 23.0821 | 5.8398
|  | 365 | 0.012167 | 0.012167 | 20.5955 | -205.955 | 0 | -5210.6622 | 0 | 252.7494 | -0.25058 | -0.056804 | -4.8283 | 231.0105 | -2.8204 | 231.0277 | -0.69955 | 5.5279 | 1.984 | 0 | 1.984 | 19.8396 | 501.9418 | 230.7388 | -2.8136 | 230.756 | 235.9768 | 235.9935 | 0.024333 | 21.5241 | 20.7756 | 1.984 | 22.7595 | 5.7582
|  | 370 | 0.012333 | 0.012333 | 20.3172 | -203.1718 | 0 | -5140.2478 | 0 | 252.7494 | -0.25058 | -0.056804 | -4.8283 | 231.0096 | -2.7822 | 231.0263 | -0.69009 | 5.5184 | 1.9538 | 0 | 1.9538 | 19.5381 | 494.3148 | 230.742 | -2.7756 | 230.7587 | 235.9792 | 235.9955 | 0.024667 | 21.2303 | 20.492 | 1.9538 | 22.4458 | 5.6788
|  | 375 | 0.0125 | 0.0125 | 20.0463 | -200.4629 | 0 | -5071.7112 | 0 | 252.7494 | -0.25058 | -0.056804 | -4.8283 | 231.0087 | -2.7451 | 231.025 | -0.6809 | 5.5092 | 1.9246 | 0 | 1.9246 | 19.2456 | 486.9134 | 230.7451 | -2.7386 | 230.7614 | 235.9815 | 235.9974 | 0.025 | 20.9443 | 20.2161 | 1.9246 | 22.1407 | 5.6016
|  | 380 | 0.012667 | 0.012667 | 19.7825 | -197.8252 | 0 | -5004.9781 | 0 | 252.7494 | -0.25058 | -0.056804 | -4.8283 | 231.0077 | -2.709 | 231.0236 | -0.67194 | 5.5003 | 1.8962 | 0 | 1.8962 | 18.9616 | 479.7278 | 230.7481 | -2.7025 | 230.7639 | 235.9838 | 235.9993 | 0.025333 | 20.666 | 19.9475 | 1.8962 | 21.8437 | 5.5265
|  | 385 | 0.012833 | 0.012833 | 19.5256 | -195.2561 | 0 | -4939.9784 | 0 | 252.7494 | -0.25058 | -0.056804 | -4.8283 | 231.0069 | -2.6738 | 231.0223 | -0.66321 | 5.4915 | 1.8686 | 0 | 1.8686 | 18.6857 | 472.7488 | 230.751 | -2.6674 | 230.7664 | 235.986 | 236.0011 | 0.025667 | 20.395 | 19.686 | 1.8686 | 21.5546 | 5.4533
|  | 390 | 0.013 | 0.013 | 19.2753 | -192.7528 | 0 | -4876.6454 | 0 | 252.7494 | -0.25058 | -0.056804 | -4.8283 | 231.006 | -2.6396 | 231.0211 | -0.65471 | 5.483 | 1.8418 | 0 | 1.8418 | 18.4177 | 465.9677 | 230.7538 | -2.6333 | 230.7688 | 235.9882 | 236.0029 | 0.026 | 20.131 | 19.4313 | 1.8418 | 21.2731 | 5.3821
|  | 395 | 0.013167 | 0.013167 | 19.0313 | -190.3129 | 0 | -4814.9157 | 0 | 252.7494 | -0.25058 | -0.056804 | -4.8283 | 231.0052 | -2.6062 | 231.0199 | -0.64643 | 5.4747 | 1.8157 | 0 | 1.8157 | 18.1572 | 459.3762 | 230.7565 | -2.5999 | 230.7712 | 235.9903 | 236.0046 | 0.026333 | 19.8738 | 19.1831 | 1.8157 | 20.9988 | 5.3127
| 1 | 400 | 0.013333 | 0.013333 | 18.7934 | -187.934 | 0 | -4754.7292 | 0 | 252.7494 | -0.25058 | -0.056804 | -4.8283 | 231.0044 | -2.5736 | 231.0187 | -0.63835 | 5.4667 | 1.7904 | 0 | 1.7904 | 17.9038 | 452.9667 | 230.7592 | -2.5674 | 230.7735 | 235.9923 | 236.0063 | 0.026667 | 19.6231 | 18.9411 | 1.7904 | 20.7315 | 5.2451
| 1 | 405 | 0.0135 | 0.0135 | 18.5614 | -185.6138 | 0 | -4696.0289 | 0 | 252.7494 | -0.25058 | -0.056804 | -4.8283 | 231.0036 | -2.5418 | 231.0175 | -0.63047 | 5.4588 | 1.7657 | 0 | 1.7657 | 17.6574 | 446.7316 | 230.7618 | -2.5358 | 230.7757 | 235.9943 | 236.0079 | 0.027 | 19.3786 | 18.7052 | 1.7657 | 20.471 | 5.1792
|  | 410 | 0.013667 | 0.013667 | 18.335 | -183.3502 | 0 | -4638.7602 | 0 | 252.7494 | -0.25058 | -0.056804 | -4.8283 | 231.0028 | -2.5108 | 231.0164 | -0.62278 | 5.4511 | 1.7418 | 0 | 1.7418 | 17.4176 | 440.6641 | 230.7643 | -2.5048 | 230.7779 | 235.9962 | 236.0095 | 0.027333 | 19.1401 | 18.4751 | 1.7418 | 20.2169 | 5.1149
|  | 415 | 0.013833 | 0.013833 | 18.1141 | -181.1412 | 0 | -4582.8715 | 0 | 252.7494 | -0.25058 | -0.056804 | -4.8283 | 231.002 | -2.4806 | 231.0154 | -0.61528 | 5.4436 | 1.7184 | 0 | 1.7184 | 17.1841 | 434.7576 | 230.7667 | -2.4747 | 230.78 | 235.9981 | 236.011 | 0.027667 | 18.9075 | 18.2506 | 1.7184 | 19.969 | 5.0522
|  | 420 | 0.014 | 0.014 | 17.8985 | -178.9847 | 0 | -4528.3135 | 0 | 252.7494 | -0.25058 | -0.056804 | -4.8283 | 231.0013 | -2.451 | 231.0143 | -0.60796 | 5.4363 | 1.6957 | 0 | 1.6957 | 16.9567 | 429.0057 | 230.7691 | -2.4452 | 230.782 | 235.9999 | 236.0126 | 0.028 | 18.6804 | 18.0315 | 1.6957 | 19.7272 | 4.991
|  | 425 | 0.014167 | 0.014167 | 17.6879 | -176.879 | 0 | -4475.0393 | 0 | 252.7494 | -0.25058 | -0.056804 | -4.8283 | 231.0006 | -2.4222 | 231.0133 | -0.6008 | 5.4291 | 1.6735 | 0 | 1.6735 | 16.7353 | 423.4026 | 230.7714 | -2.4165 | 230.7841 | 236.0017 | 236.014 | 0.028333 | 18.4587 | 17.8176 | 1.6735 | 19.4911 | 4.9313
|  | 430 | 0.014333 | 0.014333 | 17.4822 | -174.8223 | 0 | -4423.0039 | 0 | 252.7494 | -0.25058 | -0.056804 | -4.8283 | 230.9999 | -2.394 | 231.0123 | -0.59382 | 5.4221 | 1.6519 | 0 | 1.6519 | 16.5195 | 417.9425 | 230.7737 | -2.3884 | 230.786 | 236.0034 | 236.0155 | 0.028667 | 18.2423 | 17.6087 | 1.6519 | 19.2606 | 4.8729
|  | 435 | 0.0145 | 0.0145 | 17.2813 | -172.8128 | 0 | -4372.1648 | 0 | 252.7494 | -0.25058 | -0.056804 | -4.8283 | 230.9992 | -2.3665 | 231.0113 | -0.587 | 5.4153 | 1.6309 | 0 | 1.6309 | 16.3091 | 412.6201 | 230.7758 | -2.3609 | 230.7879 | 236.0051 | 236.0169 | 0.029 | 18.0308 | 17.4047 | 1.6309 | 19.0356 | 4.816
|  | 440 | 0.014667 | 0.014667 | 17.0849 | -170.8491 | 0 | -4322.4811 | 0 | 252.7494 | -0.25058 | -0.056804 | -4.8283 | 230.9985 | -2.3396 | 231.0104 | -0.58033 | 5.4086 | 1.6104 | 0 | 1.6104 | 16.104 | 407.4304 | 230.778 | -2.3341 | 230.7898 | 236.0067 | 236.0182 | 0.029333 | 17.8243 | 17.2053 | 1.6104 | 18.8157 | 4.7604
|  | 445 | 0.014833 | 0.014833 | 16.8929 | -168.9294 | 0 | -4273.9139 | 0 | 252.7494 | -0.25058 | -0.056804 | -4.8283 | 230.9979 | -2.3133 | 231.0094 | -0.57381 | 5.4021 | 1.5904 | 0 | 1.5904 | 15.9039 | 402.3684 | 230.7801 | -2.3079 | 230.7916 | 236.0083 | 236.0196 | 0.029667 | 17.6224 | 17.0104 | 1.5904 | 18.6008 | 4.706
|  | 450 | 0.015 | 0.015 | 16.7052 | -167.0524 | 0 | -4226.426 | 0 | 252.7494 | -0.25058 | -0.056804 | -4.8283 | 230.9972 | -2.2876 | 231.0085 | -0.56743 | 5.3957 | 1.5709 | 0 | 1.5709 | 15.7087 | 397.4295 | 230.7821 | -2.2822 | 230.7934 | 236.0098 | 236.0209 | 0.03 | 17.425 | 16.82 | 1.5709 | 18.3908 | 4.6529
|  | 455 | 0.015167 | 0.015167 | 16.5217 | -165.2167 | 0 | -4179.9817 | 0 | 252.7494 | -0.25058 | -0.056804 | -4.8283 | 230.9966 | -2.2625 | 231.0077 | -0.5612 | 5.3895 | 1.5518 | 0 | 1.5518 | 15.5182 | 392.6093 | 230.7841 | -2.2572 | 230.7951 | 236.0114 | 236.0221 | 0.030333 | 17.232 | 16.6337 | 1.5518 | 18.1855 | 4.6009
|  | 460 | 0.015333 | 0.015333 | 16.3421 | -163.4208 | 0 | -4134.5471 | 0 | 252.7494 | -0.25058 | -0.056804 | -4.8283 | 230.996 | -2.2379 | 231.0068 | -0.5551 | 5.3834 | 1.5332 | 0 | 1.5332 | 15.3322 | 387.9037 | 230.786 | -2.2326 | 230.7968 | 236.0128 | 236.0234 | 0.030667 | 17.0432 | 16.4515 | 1.5332 | 17.9848 | 4.5501
|  | 465 | 0.0155 | 0.0155 | 16.1664 | -161.6636 | 0 | -4090.0897 | 0 | 252.7494 | -0.25058 | -0.056804 | -4.8283 | 230.9954 | -2.2138 | 231.006 | -0.54913 | 5.3774 | 1.5151 | 0 | 1.5151 | 15.1505 | 383.3085 | 230.7879 | -2.2086 | 230.7985 | 236.0143 | 236.0246 | 0.031 | 16.8585 | 16.2733 | 1.5151 | 17.7884 | 4.5005
|  | 470 | 0.015667 | 0.015667 | 15.9944 | -159.9438 | 0 | -4046.5781 | 0 | 252.7494 | -0.25058 | -0.056804 | -4.8283 | 230.9948 | -2.1903 | 231.0052 | -0.54329 | 5.3716 | 1.4973 | 0 | 1.4973 | 14.9731 | 378.8201 | 230.7897 | -2.1851 | 230.8001 | 236.0157 | 236.0258 | 0.031333 | 16.6778 | 16.0989 | 1.4973 | 17.5962 | 4.4518
|  | 475 | 0.015833 | 0.015833 | 15.826 | -158.2602 | 0 | -4003.9825 | 0 | 252.7494 | -0.25058 | -0.056804 | -4.8283 | 230.9942 | -2.1672 | 231.0044 | -0.53757 | 5.3659 | 1.48 | 0 | 1.48 | 14.7998 | 374.4347 | 230.7915 | -2.1622 | 230.8017 | 236.0171 | 236.027 | 0.031667 | 16.5009 | 15.9282 | 1.48 | 17.4082 | 4.4043
|  | 480 | 0.016 | 0.016 | 15.6612 | -156.6116 | 0 | -3962.2743 | 0 | 252.7494 | -0.25058 | -0.056804 | -4.8283 | 230.9936 | -2.1446 | 231.0036 | -0.53197 | 5.3603 | 1.463 | 0 | 1.463 | 14.6304 | 370.1488 | 230.7933 | -2.1396 | 230.8032 | 236.0184 | 236.0281 | 0.032 | 16.3278 | 15.7611 | 1.463 | 17.2242 | 4.3577
|  | 485 | 0.016167 | 0.016167 | 15.4997 | -154.9971 | 0 | -3921.4262 | 0 | 252.7494 | -0.25058 | -0.056804 | -4.8283 | 230.9931 | -2.1225 | 231.0028 | -0.52649 | 5.3548 | 1.4465 | 0 | 1.4465 | 14.4648 | 365.9592 | 230.795 | -2.1176 | 230.8047 | 236.0197 | 236.0292 | 0.032333 | 16.1582 | 15.5975 | 1.4465 | 17.044 | 4.3121
|  | 490 | 0.016333 | 0.016333 | 15.3415 | -153.4155 | 0 | -3881.4116 | 0 | 252.7494 | -0.25058 | -0.056804 | -4.8283 | 230.9925 | -2.1009 | 231.0021 | -0.52112 | 5.3494 | 1.4303 | 0 | 1.4303 | 14.3029 | 361.8626 | 230.7967 | -2.096 | 230.8062 | 236.021 | 236.0303 | 0.032667 | 15.9921 | 15.4372 | 1.4303 | 16.8675 | 4.2675
|  | 495 | 0.0165 | 0.0165 | 15.1866 | -151.8658 | 0 | -3842.2054 | 0 | 252.7494 | -0.25058 | -0.056804 | -4.8283 | 230.992 | -2.0797 | 231.0014 | -0.51586 | 5.3442 | 1.4145 | 0 | 1.4145 | 14.1445 | 357.8561 | 230.7983 | -2.0748 | 230.8076 | 236.0222 | 236.0314 | 0.033 | 15.8295 | 15.2802 | 1.4145 | 16.6946 | 4.2237
|  | 500 | 0.016667 | 0.016667 | 15.0347 | -150.3472 | 0 | -3803.7834 | 0 | 252.7494 | -0.25058 | -0.056804 | -4.8283 | 230.9915 | -2.0589 | 231.0007 | -0.5107 | 5.339 | 1.399 | 0 | 1.399 | 13.9896 | 353.9366 | 230.7999 | -2.0541 | 230.8091 | 236.0235 | 236.0324 | 0.033333 | 15.67 | 15.1264 | 1.399 | 16.5253 | 4.1809